## Motors
Loc | Controller | IP | Axis | Name | Sys | Dev | Slits? | Motor Type | Encoder Type | 2nd Encoder Type | Closed Loop? | Reversed? | Auto On? | Steps/rev | uSteps/step | Gear Ratio (1:x) | Pitch (units/rev) | Motor Res (steps/unit) | Encoder (cts/unit) | Units | Limits as Home | Precision | Upper Lim (units) | Lower Lim (units) | Vel (units/sec) | Accel (msec to vel) | Backlash (units) | Pos at Home (units) | Home to Limit | Travel Length (units)
Test | 0 | xf19id2-galil13.nsls2.bnl.local | E | Omega | XF:19IDC-TST | {Gon:1-Ax:O} |  | High active stepper | Reverse Quadrature |  | Yes |  | Yes | 200 | 16 | 1 | 0.0027778 | 8.8889 | 11.1111 | deg | Yes | 3 |  |  | 360 | 50
|  |  | F | X | XF:19IDC-TST | {Gon:1-Ax:X} |  | High active stepper |  |  | No | Yes | Yes | 200 | 16 | 1 | 0.0027778 | 8.8889 |  | deg | Yes | 3 |  |  | 360 | 50
LCC2 | 11 | xf19id2-galil11.nsls2.bnl.local | A | BPM 1 X | XF:19IDC-OP | {BPM:1-Ax:X} |  | Reverse high active stepper | Normal Quadrature |  | No |  | Yes | 400 | 64 | 1 | 2 | 51200 |  | mm | Yes | 3 |  |  | 0.5 |  |  |  |  | 6.31
|  |  | B | BPM 1 Y | XF:19IDC-OP | {BPM:1-Ax:Y} |  | Reverse high active stepper | Normal Quadrature |  | No |  | Yes | 400 | 64 | 1 | 2 | 51200 |  | mm | Yes | 3 |  |  | 0.5 |  |  |  |  | 6.771
|  |  | C | Beam Mask X | XF:19IDC-OP | {BM:1-Ax:X} |  | High active stepper | Normal Quadrature |  | No |  | Yes | 200 | 64 | 25 | 1 | 320000 | 10000 | mm | Yes | 3 | 1.02 | -1.12 | 0.3 | 50 |  | 0.28 | Positive | 2
|  |  | D | Beam Mask Y | XF:19IDC-OP | {BM:1-Ax:Y} |  | High active stepper | Normal Quadrature |  | No |  | Yes | 200 | 64 | 25 | 1 | 320000 | 10000 | mm | Yes | 3 | 0.62 | -1.02 | 0.3 | 50 |  | 0.08 | Positive | 2
|  |  | E | Slit WB Inboard | XF:19IDC-OP | {Slt:WB-Ax:I} | X- | Reverse high active stepper | Normal Quadrature |  | Yes | Yes | Yes | 200 | 64 | 10 | 1 | 128000 | 10000 | mm | Yes | 3 | 4.02 | -4.02 | 0.2 | 50 |  |  | Positive | 24
|  |  | F | Slit WB Outboard | XF:19IDC-OP | {Slt:WB-Ax:O} | X+ | Reverse high active stepper | Normal Quadrature |  | Yes | Yes | Yes | 200 | 64 | 10 | 1 | 128000 | 10000 | mm | Yes | 3 | 4.02 | -4.02 | 0.2 | 50 |  |  | Positive | 24
|  |  | G | Slit WB Top | XF:19IDC-OP | {Slt:WB-Ax:T} | Y+ | Reverse high active stepper | Normal Quadrature |  | Yes |  | Yes | 200 | 64 | 10 | 1 | 128000 | 10000 | mm | Yes | 3 | 4.02 | -4.02 | 0.2 | 50 |  | 5.84 | Positive | 8
|  |  | H | Slit WB Botom | XF:19IDC-OP | {Slt:WB-Ax:B} | Y- | Reverse high active stepper | Normal Quadrature |  | Yes |  | Yes | 200 | 64 | 10 | 1 | 128000 | 10000 | mm | Yes | 3 | 4.2 | -4.2 | 0.2 | 50 |  | 2.16 | Positive | 8
LCC3 | 9 | xf19id2-galil9.nsls2.bnl.local | A | BPM 2 X | XF:19IDC-OP | {BPM:2-Ax:X} |  | Low active stepper | Normal Quadrature |  | No |  | Yes | 200 | 64 |  |  |  |  | mm | Yes | 3
|  |  | B | BPM 2 Y | XF:19IDC-OP | {BPM:2-Ax:Y} |  | Low active stepper | Normal Quadrature |  | No |  | Yes | 200 | 64 |  |  |  |  | mm | Yes | 3
|  |  | C | [16 empty] | mm | Yes | 3
|  |  | D | Mono Bragg | XF:19IDC-OP | {Mono:DCM-Ax:B} |  | Servo | Reverse Quadrature | Reverse Quadrature | Yes |  | No | 1 | 1 |  |  |  | 1000000 | deg | Yes | 3 | 40 | 0 | 0.1 | 50
LCC3 | 10 | xf19id2-galil10.nsls2.bnl.local | A | Mono C2 Perp | XF:19IDC-OP | {Mono:DCM-Ax:Perp} |  | High active stepper | Reverse Quadrature |  | Yes |  | Yes | 200 | 16 | 16 | 1 | 51200 | 20000 | mm | Yes | 3 | 20 | 3 | 0.4 | 50 |  | 7.79 | Positive | 17
|  |  | B | Mono C2 Para | XF:19IDC-OP | {Mono:DCM-Ax:Para} |  | High active stepper | Reverse Quadrature |  | Yes |  | Yes | 200 | 16 | 8 | 1 | 25600 | 20000 | mm | Yes | 3 | 125 | 35 | 1 | 30 |  | 78.4 | Positive | 90
|  |  | C | Mono C2 Pitch | XF:19IDC-OP | {Mono:DCM-Ax:P} |  | High active stepper | Normal Quadrature |  | No |  | Yes | 200 | 16 | 49 | 1 | 156800 | 2460 | mrad | Yes | 3 | 10 | -15 | 0.2 | 50 |  | 14.88 | Positive | 25
|  |  | D | Mono C2 Roll | XF:19IDC-OP | {Mono:DCM-Ax:R} |  | Reverse high active stepper | Reverse Quadrature |  | No |  | Yes | 200 | 16 | 49 | 1 | 156800 | 2460 | mrad | Yes | 3 | 1.5 | -20 | 0.2 | 45 |  |  |  | 21.5
|  |  | E | Mono C2 Yaw | XF:19IDC-OP | {Mono:DCM-Ax:Yaw} |  | Reverse high active stepper | Normal Quadrature |  | No |  | Yes | 200 | 16 | 49 | 2 | 313600 |  | mrad | Yes | 3 | 0 | -5 | 0.02 | 20 |  |  |  | 5
|  |  | F | Mono C2 Bend 1 | XF:19IDC-OP | {Mono:DCM-Ax:Bnd1} |  | Reverse high active stepper | Normal Quadrature |  | No |  | Yes | 200 | 16 | 28 | 2 | 179200 |  | mm | Yes | 3 | 1.1 | 0 | 0.045 | 10 |  |  |  | 1.3
|  |  | G | Mono C2 Bend 2 | XF:19IDC-OP | {Mono:DCM-Ax:Bnd2} |  | Reverse high active stepper | Normal Quadrature |  | No |  | Yes | 200 | 16 | 28 | 2 | 179200 |  | mm | Yes | 3 | 1.1 | 0 | 0.045 | 10 |  |  |  | 1.3
|  |  | H | Mono C1 Bend | XF:19IDC-OP | {Mono:DCM-Ax:Bnd} |  | Reverse high active stepper | Normal Quadrature |  | No |  | Yes | 200 | 16 | 28 | 0.5 | 44800 |  | mm | Yes | 3 | 6.8 | 5.7 | 0.1565 | 10 |  |  |  | 1.1
LCC4 | 7 | xf19id2-galil7.nsls2.bnl.local | A | Mirror Vertical | XF:19IDC-OP | {Mir:1-Ax:Y} |  | Reverse high active stepper | Normal Quadrature |  | Yes |  | Yes | 200 | 64 | 320 | 5 | 20480000 | 10000 | mm | Yes | 3 | 6.3 | -13.7 | 0.08 | 100 |  |  |  | 20
|  |  | B | Mirror Horizontal | XF:19IDC-OP | {Mir:1-Ax:X} |  | Reverse high active stepper | Normal Quadrature |  | Yes |  | Yes | 200 | 64 | 100 | 2 | 2560000 | 10000 | mm | Yes | 3 | 10 | -10 | 0.1 | 70 |  |  |  | 20
|  |  | C | Mirror Pitch | XF:19IDC-OP | {Mir:1-Ax:P} |  | Reverse high active stepper | Normal Quadrature |  | Yes |  | Yes | 200 | 64 | 100 | 2 | 2560000 | 6000 | mm | Yes | 3 | 17.84 | -17.82 | 0.17 | 70 |  |  |  | 35
|  |  | D | Mirror Roll | XF:19IDC-OP | {Mir:1-Ax:R} |  | Reverse high active stepper | Normal Quadrature |  | Yes |  | Yes | 200 | 64 | 100 | 2 | 2560000 | 6000 | mm | Yes | 3 | 17.99 | -17.89 | 0.17 | 70 |  |  |  | 36
|  |  | E | Mirror Bend 1 | XF:19IDC-OP | {Mir:1-Ax:Bnd1} |  | Reverse high active stepper | Normal Quadrature |  | No |  | Yes | 200 | 1 |  |  | 26667 |  | mm | Yes | 3 | 7.5 | -0.1 | 0.015 | 100 |  |  |  | 7.6
|  |  | F | Mirror Bend 2 | XF:19IDC-OP | {Mir:1-Ax:Bnd2} |  | Reverse high active stepper | Normal Quadrature |  | No |  | Yes | 200 | 1 |  |  | 26667 |  | mm | Yes | 3 | 7 | -0.1 | 0.015 | 100 |  |  |  | 7.1
|  |  | G | BPM 3 X | XF:19IDC-OP | {BPM:3-Ax:X} |  | Reverse high active stepper | Normal Quadrature |  | No |  | Yes | 200 | 64 |  |  |  |  | mm | Yes | 3
|  |  | H | BPM 3 Y | XF:19IDC-OP | {BPM:3-Ax:Y} |  | Reverse high active stepper | Normal Quadrature |  | No |  | Yes | 200 | 64 |  |  |  |  | mm | Yes | 3
LCC4 | 8 | xf19id2-galil8.nsls2.bnl.local | A | Slit MB Top | XF:19IDC-OP | {Slt:MB-Ax:T} | Y+ | Reverse high active stepper | Reverse Quadrature |  | Yes |  | Yes | 200 | 16 |  | 1 |  | 10000 | mm | Yes | 3 | 10 | -10 | 0.5 | 100 |  | 10.43 | Positive | 20
|  |  | B | Slit MB Bottom | XF:19IDC-OP | {Slt:MB-Ax:B} | Y- | Reverse high active stepper | Reverse Quadrature |  | Yes |  | Yes | 200 | 16 |  | 1 |  | 10000 | mm | Yes | 3 | 10 | -10 | 0.5 | 100 |  |  |  | 20
|  |  | C | Slit MB Inboard | XF:19IDC-OP | {Slt:MB-Ax:I} | X- | High active stepper | Normal Quadrature |  | Yes | Yes | Yes | 200 | 16 |  | 1 |  | 10000 | mm | Yes | 3 | 10 | -10 | 0.5 | 100 |  | 11.68 | Positive | 20
|  |  | D | Slit MB Outboard | XF:19IDC-OP | {Slt:MB-Ax:O} | X+ | High active stepper | Normal Quadrature |  | Yes | Yes | Yes | 200 | 16 |  | 1 |  | 10000 | mm | Yes | 3 | 10 | -10 | 0.5 | 100 |  |  |  | 20
ES | 1 | xf19id2-galil1.nsls2.bnl.local | A | Cam HiMag Z | XF:19IDC-ES | {Cam:HiMag-Ax:Z} |  | Low active stepper | Normal Quadrature |  | No |  | Yes | 200 | 64 | 1 | 1 | 12800 |  | mm | Yes | 3 |  |  | 10 | 100
|  |  | B | Cam HiMag X | XF:19IDC-ES | {Cam:HiMag-Ax:X} |  | Low active stepper | Normal Quadrature |  | No | Yes | Yes | 200 | 64 | 1 | 1 | 12800 |  | mm | Yes | 3 |  |  | 10 | 100
|  |  | C | Cam HiMag Focus | XF:19IDC-ES | {Cam:HiMag-Ax:F} |  | Reverse low active stepper | Normal Quadrature |  | No |  | Yes | 24 | 64 | 0.0038254 | 1 | 5.8758 |  | mm | Yes | 3 |  |  | 10 | 100
|  |  | D | Cam LoMag Z | XF:19IDC-ES | {Cam:LoMag-Ax:Z} |  | Low active stepper | Normal Quadrature |  | No |  | Yes | 200 | 64 | 1 | 1 | 12800 |  | mm | Yes | 3 |  |  | 10 | 100
|  |  | E | Cam LoMag X | XF:19IDC-ES | {Cam:LoMag-Ax:X} |  | Low active stepper | Normal Quadrature |  | No | Yes | Yes | 200 | 64 | 1 | 1 | 12800 |  | mm | Yes | 3 |  |  | 10 | 100
|  |  | F | Cam LoMag Focus | XF:19IDC-ES | {Cam:LoMag-Ax:F} |  | Reverse low active stepper | Normal Quadrature |  | No |  | Yes | 24 | 64 | 0.0038254 | 1 | 5.8758 |  | mm | Yes | 3 |  |  | 10 | 100
|  |  | G | Beam Pipe Pitch | XF:19IDC-ES | {BP:1-Ax:P} |  | Reverse low active stepper | Normal Quadrature |  | No | Yes | Yes | 200 | 64 | 1 | 1.5875 | 30075 |  | deg | Yes | 3 |  |  | 10 | 100
|  |  | H | Global Yaw | XF:19IDC-ES | {Glb:1-Ax:Yaw} |  | Reverse low active stepper | Normal Quadrature |  | No | Yes | Yes | 200 | 64 | 1 | 1.5875 | 71047 |  | deg | Yes | 3 |  |  | 10 | 100
ES | 2 | xf19id2-galil2.nsls2.bnl.local | A | Omega | XF:19IDC-ES | {Gon:1-Ax:O} |  | Servo | Normal Quadrature | Normal Quadrature | Yes |  | No | 1 | 1 | 1 |  | 10000 | 10000 | deg | Yes | 3 |  |  | 10 | 100
|  |  | B | Sample Vert | XF:19IDC-ES | {Gon:1-Ax:V} |  | Reverse low active stepper | Normal Quadrature |  | No |  | Yes | 200 | 500 | 10 | 5 | 20000 | 20000 | mm | Yes | 3 |  |  | 10 | 100
|  |  | C | Optic Vert | XF:19IDC-ES | {Opt:1-Ax:V} |  | Reverse low active stepper | Normal Quadrature |  | No |  | Yes | 200 | 500 | 10 | 5 | 20000 | 20000 | mm | Yes | 3 |  |  | 10 | 100
|  |  | D | Global X | XF:19IDC-ES | {Glb:1-Ax:X} |  | Low active stepper | Normal Quadrature |  | No |  | Yes | 200 | 64 | 1 | 1 | 12800 |  | mm | Yes | 3 |  |  | 10 | 100
|  |  | E | Sample X | XF:19IDC-ES | {Gon:1-Ax:X} |  | Low active stepper | Normal Quadrature |  | No |  | Yes | 200 | 64 | 1 | 1 | 12800 |  | mm | No | 3 |  |  | 1 | 100
|  |  | F | Sample Y | XF:19IDC-ES | {Gon:1-Ax:Y} |  | Low active stepper | Normal Quadrature |  | No |  | Yes | 200 | 64 | 1 | 1 | 12800 |  | mm | No | 3 |  |  | 1 | 100
|  |  | G | Sample Z | XF:19IDC-ES | {Gon:1-Ax:Z} |  | Reverse low active stepper | Normal Quadrature |  | No |  | Yes | 200 | 64 | 1 | 0.635 | 20151 |  | mm | No | 3 |  |  | 0.5 | 100
|  |  | H | Kappa | XF:19IDC-ES | {Gon:1-Ax:K} |  | Reverse low active stepper | Normal Quadrature |  | No |  | Yes | 24 | 64 | 0.0071043 | 1 | 600.572 |  | deg | Yes | 3 |  |  | 10 | 100
ES | 3 | xf19id2-galil3.nsls2.bnl.local | A | Beam Stop V | XF:19IDC-ES | {BS:1-Ax:V} |  | Low active stepper | Normal Quadrature |  | No |  | Yes | 200 | 64 | 1 | 0.3048 | 41995 |  | mm | Yes | 3 |  |  | 10 | 100
|  |  | B | Beam Stop H | XF:19IDC-ES | {BS:1-Ax:H} |  | Low active stepper | Normal Quadrature |  | No |  | Yes | 200 | 64 | 40 | 1 | 1422.222 |  | deg | Yes | 3 |  |  | 10 | 100
|  |  | C | Beam Stop Z | XF:19IDC-ES | {BS:1-Ax:Z} |  | Reverse low active stepper | Normal Quadrature |  | No |  | Yes | 200 | 64 | 1 | 2 | 6400 |  | mm | Yes | 3 |  |  | 10 | 100
|  |  | D | Slit Beam Def Bottom | XF:19IDC-ES | {Slt:BD-Ax:B} |  | Low active stepper | Normal Quadrature |  | No |  | Yes | 24 | 64 | 0.0071043 | 1 | 600.572 |  | deg | Yes | 3 |  |  | 10 | 100
|  |  | E | Slit Beam Def Top | XF:19IDC-ES | {Slt:BD-Ax:T} |  | Reverse low active stepper | Normal Quadrature |  | No |  | Yes | 24 | 64 | 0.0071043 | 1 | 600.572 |  | deg | Yes | 3 |  |  | 10 | 100
|  |  | F | Slit Beam Def Inboard | XF:19IDC-ES | {Slt:BD-Ax:I} |  | Low active stepper | Normal Quadrature |  | No |  | Yes | 24 | 64 | 0.0071043 | 1 | 600.572 |  | deg | Yes | 3 |  |  | 10 | 100
|  |  | G | Slit Beam Def Outboard | XF:19IDC-ES | {Slt:BD-Ax:O} |  | Reverse low active stepper | Normal Quadrature |  | No |  | Yes | 24 | 64 | 0.0071043 | 1 | 600.572 |  | deg | Yes | 3 |  |  | 10 | 100
|  |  | H | [18 empty] | 3
ES | 5 | xf19id2-galil5.nsls2.bnl.local | A | Detector Z | XF:19IDC-ES | {Det:1-Ax:Z} |  | Reverse low active stepper | Normal Quadrature |  | No |  | Yes | 200 | 500 | 60 | 6.35 | 20000 |  | mm | Yes | 3 |  |  | 5 | 2000 | 0.4
|  |  | B | Table Vert Center | XF:19IDC-ES | {Tbl:1-Ax:VCtr} |  | Low active stepper | Normal Quadrature |  | No |  | Yes | 200 | 500 | 60 | 6.35 | 94488 |  | mm | Yes | 3 |  |  | 10 | 100
|  |  | C | Table Vert Outboard | XF:19IDC-ES | {Tbl:1-Ax:VO} |  | Reverse low active stepper | Normal Quadrature |  | No |  | Yes | 200 | 500 | 60 | 6.35 | 94488 |  | mm | Yes | 3 |  |  | 10 | 100
|  |  | D | Table Vert Inboard | XF:19IDC-ES | {Tbl:1-Ax:VI} |  | Low active stepper | Normal Quadrature |  | No |  | Yes | 200 | 500 | 10 | 5 | 20000 |  | mm | Yes | 3 |  |  | 10 | 100
|  |  | E | Table Horiz Upstream | XF:19IDC-ES | {Tbl:1-Ax:HU} |  | Low active stepper | Normal Quadrature |  | No |  | Yes | 200 | 500 | 10 | 5 | 20000 |  | mm | Yes | 3 |  |  | 10 | 100
|  |  | F | Table Horiz Downstream | XF:19IDC-ES | {Tbl:1-Ax:HD} |  | Low active stepper | Normal Quadrature |  | No |  | Yes | 200 | 500 | 10 | 5 | 20000 |  | mm | Yes | 3 |  |  | 10 | 100

## Vector
Loc | Controller | P | R | Index | Axis | EGU
Test | 0 | XF:19IDC-TST | {Gon:1- | 0 | O | deg
|  |  |  | 1 | X | mm
ES | 2 | XF:19IDC-ES | {Gon:1- | 0 | O | deg
|  |  |  | 1 | X | mm
|  |  |  | 2 | Y | mm
|  |  |  | 3 | Z | mm

## Temperatures
Loc | Controller | Analog Input | Motor | Formula | EGU | PREC
Test | 0 | 4 | XF:19IDC-OP{Test-Ax:E} | A*1000/10.15 | C | 3
|  | 5 | XF:19IDC-OP{Test-Ax:F} | A*1000/10.15 | C | 3
LCC3 | 10 | 0 | XF:19IDC-OP{Mono:DCM-Ax:P} | A*1000/10.15 | C | 3
|  | 1 | XF:19IDC-OP{Mono:DCM-Ax:R} | A*1000/10.15 | C | 3
|  | 2 | XF:19IDC-OP{Mono:DCM-Ax:Para} | A*1000/10.15 | C | 3
|  | 3 | XF:19IDC-OP{Mono:DCM-Ax:Bnd2} | A*1000/10.15 | C | 3
|  | 4 | XF:19IDC-OP{Mono:DCM-Ax:Bnd} | A*1000/10.15 | C | 3
|  | 5 | XF:19IDC-OP{Mono:DCM-Ax:Yaw} | A*1000/10.15 | C | 3

## Digital Outputs
Loc | Controller | Digital Output | Name | ZNAM | ONAM
Test | 0 | 13 | SHUT | Off | On
ES | 2 | 13 | SHUT | Close | Open

## Motor Types
Motor Type | IOC Setting | Galil Setting
Servo | 0 | 1
Reverse servo | 1 | -1
High active stepper | 2 | -2
Low active stepper | 3 | 2
Reverse high active stepper | 4 | -2.5
Reverse low active stepper | 5 | 2.5

## Encoder Types
Encoder Type | IOC Setting
Normal Quadrature | 0
Pulse and Dir | 1
Reverse Quadrature | 2
Rev Pulse and Dir | 3